## Cover
FoxIoT 6ADi4Ro2AVo2AIo Modbus Integration Guide
Register Map, Rule Configuration, Firmware Update, and Example Packets
Software Version 1.03
FoxIoT OÜ ¦ www.foxiot.eu ¦ support@foxiot.eu |  | Document Version: 1.1

## Introduction
Modbus Integration Guide
This guide provides detailed information for integrating the FoxIoT 6ADi4Ro2AVo2AIo controller with Modbus-based systems. It includes a complete register map with descriptions, data types, default values, scaling factors, and access levels. In addition, the guide outlines how to configure Modbus settings, use the built-in rule engine via Modbus, perform firmware updates, and construct Modbus RTU request/response examples for reading and writing registers. For general information about the Modbus protocol, visit the official Modbus website:
(http://www.modbus.org)
Data Types Description
Data Type | Description
INT16 | 16-bit signed integer
UINT16 | 16-bit unsigned integer.
UINT32 | 32-bit unsigned integer.
UINT64 | 64-bit unsigned integer.
FLOAT | 32-bit floating-point number.
Access Level Description
Access Level | Description
RO (Read-Only) | This access level indicates that the register can only be read and not modified.
RW (Read-Write) | Registers with this access level can be both read and modified by the user.
W (Write-Only) | Registers with this access level can only be write by the user.
Holding Registers and Applicable Function Codes
All registers listed in the table below are holding registers.
Function Code | Description
Function Code 03 (0x03) | Read Holding Registers. This function code is used to read the contents of one or more holding registers.
Function Code 06 (0x06) | Write Single Register. This function code is used to write a value into a single holding register.
Function Code 16 (0x10) | Write Multiple Registers. This function code allows writing values to multiple holding registers in a single command.
Understanding the Modbus Register Map
Column name | Description
Register Address | The starting Modbus register offset. For example, address 0 corresponds to register 40001 in Modbus convention. (Note: The register numbers in this document refer to Modbus addresses, which begin at 0.)
Register Type | Indicates the type of Modbus register (e.g., Holding Register).
Name/Label | A human-readable identifier describing the data point (e.g., Serial Number, Input Voltage).
Data Type | Specifies how the data is encoded (e.g., INT16, UINT16, UINT32, UINT64, or FLOAT). The data type also determines how many 16-bit registers are used to represent the value.
Access Level | Indicates whether the register is Read-Only (RO) or Read/Write (RW).
Default Value | The initial value set at factory or during device boot-up, where applicable.
Value Range | The valid range of values. Useful for validation.
Units of Measure | Specifies the physical unit of the value (e.g., Volts, Seconds).
Scaling Factor | Multiplier applied to the raw register value to obtain the actual value (e.g., a factor of 0.01 means the register value must be multiplied by 0.01)
Size | Number of 16-bit Modbus registers used for this data item.
Description | Provides additional details for understanding or using the register value.

## Modbus Registers
Register Address | Register Type | Name/Label | Data Type | Access Level | Default Value | Value Range | Units of Measure | Scaling Factor | Size | Description
Readable Registers
0 | Holding | Serial Number | UINT64 | RO | - | - | - | 1 | 4 | Device's unique identifier
4 | Holding | Software Version | UINT16 | RO | - | - | - | 1 | 1 | Major.Minor format; MSB=Major, LSB=Minor. E.g., 0x0104 = v1.4
5 | Holding | Hardware Version | UINT16 | RO | - | - | - | 1 | 1 | Major.Minor format; MSB=Major, LSB=Minor. E.g., 0x0101 = v1.1
6 | Holding | Platform Number | UINT16 | RO | 35 | - | - | 1 | 1 | Unique identifier (35 for this product) for distinguishing among different platforms/products within the same family. Used for compatibility checks.
8 | Holding | Uptime | UINT32 | RO | - | 0 to 4294967295 | Seconds | 1 | 2 | Controller uptime since last boot in seconds.
10 | Holding | Input Voltage | FLOAT | RO | - | 0 to 32.0 | Volts | 1 | 2 | Input Voltage in Volts, float representation.
12 | Holding | Input Voltage | UINT16 | RO | - | 0 to 3200 | Volts | 0.01 | 1 | Input Voltage in Volts, UINT16 scaled by 0.01 for decimal representation.
30 | Holding | Input 1 - Analog | FLOAT | RO | - | 0 to 10.0V | Volts | 1 | 2 | Floating-point voltage reading from Input 1. Valid when Input Mode 1 (Reg 266) is set to any input mode expect NTC.
32 | Holding | Input 2 - Analog | FLOAT | RO | - | 0 to 10.0V | Volts | 1 | 2 | Floating-point voltage reading from Input 2. Valid when Input Mode 2 (Reg 267) is set to any input mode expect NTC.
34 | Holding | Input 3 - Analog | FLOAT | RO | - | 0 to 10.0V | Volts | 1 | 2 | Floating-point voltage reading from Input 3. Valid when Input Mode 3 (Reg 268) is set to any input mode expect NTC.
36 | Holding | Input 4 - Analog | FLOAT | RO | - | 0 to 10.0V | Volts | 1 | 2 | Floating-point voltage reading from Input 4. Valid when Input Mode 4 (Reg 269) is set to any input mode expect NTC.
38 | Holding | Input 5 - Analog | FLOAT | RO | - | 0 to 10.0V | Volts | 1 | 2 | Floating-point voltage reading from Input 5. Valid when Input Mode 5 (Reg 270) is set to any input mode expect NTC.
40 | Holding | Input 6 - Analog | FLOAT | RO | - | 0 to 10.0V | Volts | 1 | 2 | Floating-point voltage reading from Input 6. Valid when Input Mode 6 (Reg 271) is set to any input mode expect NTC.
42 | Holding | Input 1 - Analog | UINT16 | RO | - | 0 to 10000 | Volts | 0.001 | 1 | Scaled UINT16 voltage reading from Input 1. Multiply by 0.001 to convert to Volts. Valid when Input Mode 1 (Reg 266) is set to any input mode except NTC.
43 | Holding | Input 2 - Analog | UINT16 | RO | - | 0 to 10000 | Volts | 0.001 | 1 | Scaled UINT16 voltage reading from Input 2. Multiply by 0.001 to convert to Volts. Valid when Input Mode 2 (Reg 267) is set to any input mode except NTC.
44 | Holding | Input 3 - Analog | UINT16 | RO | - | 0 to 10000 | Volts | 0.001 | 1 | Scaled UINT16 voltage reading from Input 3. Multiply by 0.001 to convert to Volts. Valid when Input Mode 3 (Reg 268) is set to any input mode except NTC.
45 | Holding | Input 4 - Analog | UINT16 | RO | - | 0 to 10000 | Volts | 0.001 | 1 | Scaled UINT16 voltage reading from Input 4. Multiply by 0.001 to convert to Volts. Valid when Input Mode 4 (Reg 269) is set to any input mode except NTC.
46 | Holding | Input 5 - Analog | UINT16 | RO | - | 0 to 10000 | Volts | 0.001 | 1 | Scaled UINT16 voltage reading from Input 5. Multiply by 0.001 to convert to Volts. Valid when Input Mode 5 (Reg 270) is set to any input mode except NTC.
47 | Holding | Input 6 - Analog | UINT16 | RO | - | 0 to 10000 | Volts | 0.001 | 1 | Scaled UINT16 voltage reading from Input 6. Multiply by 0.001 to convert to Volts. Valid when Input Mode 6 (Reg 271) is set to any input mode except NTC.
48 | Holding | Input 1 - Digital | UINT16 | RO | - | 0 to 1 | - | 1 | 1 | Represents the state of Input 1. See Note *1 for active/inactive state description. Valid when Input Mode 1 (Reg 266) is set to any input mode except NTC.
49 | Holding | Input 2 - Digital | UINT16 | RO | - | 0 to 1 | - | 1 | 1 | Represents the state of Input 2. See Note *1 for active/inactive state description. Valid when Input Mode 2 (Reg 267) is set to any input mode except NTC.
50 | Holding | Input 3 - Digital | UINT16 | RO | - | 0 to 1 | - | 1 | 1 | Represents the state of Input 3. See Note *1 for active/inactive state description. Valid when Input Mode 3 (Reg 268) is set to any input mode except NTC.
51 | Holding | Input 4 - Digital | UINT16 | RO | - | 0 to 1 | - | 1 | 1 | Represents the state of Input 4. See Note *1 for active/inactive state description. Valid when Input Mode 4 (Reg 269) is set to any input mode except NTC.
52 | Holding | Input 5 - Digital | UINT16 | RO | - | 0 to 1 | - | 1 | 1 | Represents the state of Input 5. See Note *1 for active/inactive state description. Valid when Input Mode 5 (Reg 270) is set to any input mode except NTC.
53 | Holding | Input 6 - Digital | UINT16 | RO | - | 0 to 1 | - | 1 | 1 | Represents the state of Input 6. See Note *1 for active/inactive state description. Valid when Input Mode 6 (Reg 271) is set to any input mode except NTC.
54 | Holding | Input 1 - Digital Customized | UINT16 | RO | - | - | - | 1 | 1 | Complex custom functionality, including click types, with real-time input tracking to ensure all changes are captured. See Note *2 for a detailed explanation and examples. Valid when Input Mode 1 (Reg 266) is set to any input mode except NTC.
55 | Holding | Input 2 - Digital Customized | UINT16 | RO | - | - | - | 1 | 1 | Complex custom functionality, including click types, with real-time input tracking to ensure all changes are captured. See Note *2 for a detailed explanation and examples. Valid when Input Mode 2 (Reg 267) is set to any input mode except NTC.
56 | Holding | Input 3 - Digital Customized | UINT16 | RO | - | - | - | 1 | 1 | Complex custom functionality, including click types, with real-time input tracking to ensure all changes are captured. See Note *2 for a detailed explanation and examples. Valid when Input Mode 3 (Reg 268) is set to any input mode except NTC.
57 | Holding | Input 4 - Digital Customized | UINT16 | RO | - | - | - | 1 | 1 | Complex custom functionality, including click types, with real-time input tracking to ensure all changes are captured. See Note *2 for a detailed explanation and examples. Valid when Input Mode 4 (Reg 269) is set to any input mode except NTC.
58 | Holding | Input 5 - Digital Customized | UINT16 | RO | - | - | - | 1 | 1 | Complex custom functionality, including click types, with real-time input tracking to ensure all changes are captured. See Note *2 for a detailed explanation and examples. Valid when Input Mode 5 (Reg 270) is set to any input mode except NTC.
59 | Holding | Input 6 - Digital Customized | UINT16 | RO | - | - | - | 1 | 1 | Complex custom functionality, including click types, with real-time input tracking to ensure all changes are captured. See Note *2 for a detailed explanation and examples. Valid when Input Mode 6 (Reg 271) is set to any input mode except NTC.
60 | Holding | Input 1 - Temperature | FLOAT | RO | - | -50.0 to 125.0 | °C | 1 | 2 | Temperature reading from Input 1, represented as a FLOAT in °C. If the input is open, the reading value is 255. Valid only when Input Mode 1 (Reg 266) is set to NTC mode.
62 | Holding | Input 2 - Temperature | FLOAT | RO | - | -50.0 to 125.0 | °C | 1 | 2 | Temperature reading from Input 2, represented as a FLOAT in °C. If the input is open, the reading value is 255. Valid only when Input Mode 2 (Reg 267) is set to NTC mode.
64 | Holding | Input 3 - Temperature | FLOAT | RO | - | -50.0 to 125.0 | °C | 1 | 2 | Temperature reading from Input 3, represented as a FLOAT in °C. If the input is open, the reading value is 255. Valid only when Input Mode 3 (Reg 268) is set to NTC mode.
66 | Holding | Input 4 - Temperature | FLOAT | RO | - | -50.0 to 125.0 | °C | 1 | 2 | Temperature reading from Input 4, represented as a FLOAT in °C. If the input is open, the reading value is 255. Valid only when Input Mode 4 (Reg 269) is set to NTC mode.
68 | Holding | Input 5 - Temperature | FLOAT | RO | - | -50.0 to 125.0 | °C | 1 | 2 | Temperature reading from Input 5, represented as a FLOAT in °C. If the input is open, the reading value is 255. Valid only when Input Mode 5 (Reg 270) is set to NTC mode.
70 | Holding | Input 6 - Temperature | FLOAT | RO | - | -50.0 to 125.0 | °C | 1 | 2 | Temperature reading from Input 6, represented as a FLOAT in °C. If the input is open, the reading value is 255. Valid only when Input Mode 6 (Reg 271) is set to NTC mode.
72 | Holding | Input 1 - Temperature | INT16 | RO | - | -5000 to 12500 | °C | 0.01 | 1 | Temperature in °C (scale by 0.01) from Input 1. If the input is open, the reading value is 25500. Valid only when Input Mode 1 (Reg 266) is set to NTC mode.
73 | Holding | Input 2 - Temperature | INT16 | RO | - | -5000 to 12500 | °C | 0.01 | 1 | Temperature in °C (scale by 0.01) from Input 2. If the input is open, the reading value is 25500. Valid only when Input Mode 2 (Reg 267) is set to NTC mode.
74 | Holding | Input 3 - Temperature | INT16 | RO | - | -5000 to 12500 | °C | 0.01 | 1 | Temperature in °C (scale by 0.01) from Input 3. If the input is open, the reading value is 25500. Valid only when Input Mode 3 (Reg 268) is set to NTC mode.
75 | Holding | Input 4 - Temperature | INT16 | RO | - | -5000 to 12500 | °C | 0.01 | 1 | Temperature in °C (scale by 0.01) from Input 4. If the input is open, the reading value is 25500. Valid only when Input Mode 4 (Reg 269) is set to NTC mode.
76 | Holding | Input 5 - Temperature | INT16 | RO | - | -5000 to 12500 | °C | 0.01 | 1 | Temperature in °C (scale by 0.01) from Input 5. If the input is open, the reading value is 25500. Valid only when Input Mode 5 (Reg 270) is set to NTC mode.
77 | Holding | Input 6 - Temperature | INT16 | RO | - | -5000 to 12500 | °C | 0.01 | 1 | Temperature in °C (scale by 0.01) from Input 6. If the input is open, the reading value is 25500. Valid only when Input Mode 6 (Reg 271) is set to NTC mode.
78 | Holding | Input 1 – Current | FLOAT | RO | - | 0 to 65535 | A | 1 | 2 | Measured input current from Input 1. Valid only when Input Mode 1 (Reg 266) is 1. Shunt resistor value (Reg 272) must match the actual shunt resistor on Input 1 (Ω).
80 | Holding | Input 2 – Current | FLOAT | RO | - | 0 to 65535 | A | 1 | 2 | Measured input current from Input 2. Valid only when Input Mode 2 (Reg 267) is 1. Shunt resistor value (Reg 273) must match the actual shunt resistor on Input 2 (Ω).
82 | Holding | Input 3 – Current | FLOAT | RO | - | 0 to 65535 | A | 1 | 2 | Measured input current from Input 3. Valid only when Input Mode 3 (Reg 268) is 1. Shunt resistor value (Reg 274) must match the actual shunt resistor on Input 3 (Ω).
84 | Holding | Input 4 – Current | FLOAT | RO | - | 0 to 65535 | A | 1 | 2 | Measured input current from Input 4. Valid only when Input Mode 4 (Reg 269) is 1. Shunt resistor value (Reg 275) must match the actual shunt resistor on Input 4 (Ω).
86 | Holding | Input 5 – Current | FLOAT | RO | - | 0 to 65535 | A | 1 | 2 | Measured input current from Input 5. Valid only when Input Mode 5 (Reg 270) is 1. Shunt resistor value (Reg 276) must match the actual shunt resistor on Input 5 (Ω).
88 | Holding | Input 6 – Current | FLOAT | RO | - | 0 to 65535 | A | 1 | 2 | Measured input current from Input 6. Valid only when Input Mode 6 (Reg 271) is 1. Shunt resistor value (Reg 277) must match the actual shunt resistor on Input 6 (Ω).
90 | Holding | Input 1 – Current | UINT16 | RO | - | 0 to 65535 | A | 0.001 | 1 | Measured input current in amperes (A) from Input 1 (scale by 0.001). Valid only when Input Mode 1 (Reg 266) is 1. Shunt resistor value (Reg 272) must match the actual shunt resistor on Input 1 (Ω).
91 | Holding | Input 2 – Current | UINT16 | RO | - | 0 to 65535 | A | 0.001 | 1 | Measured input current in amperes (A) from Input 2 (scale by 0.001). Valid only when Input Mode 2 (Reg 267) is 1. Shunt resistor value (Reg 273) must match the actual shunt resistor on Input 2 (Ω).
92 | Holding | Input 3 – Current | UINT16 | RO | - | 0 to 65535 | A | 0.001 | 1 | Measured input current in amperes (A) from Input 3 (scale by 0.001). Valid only when Input Mode 3 (Reg 268) is 1. Shunt resistor value (Reg 274) must match the actual shunt resistor on Input 3 (Ω).
93 | Holding | Input 4 – Current | UINT16 | RO | - | 0 to 65535 | A | 0.001 | 1 | Measured input current in amperes (A) from Input 4 (scale by 0.001). Valid only when Input Mode 4 (Reg 269) is 1. Shunt resistor value (Reg 275) must match the actual shunt resistor on Input 4 (Ω).
94 | Holding | Input 5 – Current | UINT16 | RO | - | 0 to 65535 | A | 0.001 | 1 | Measured input current in amperes (A) from Input 5 (scale by 0.001). Valid only when Input Mode 5 (Reg 270) is 1. Shunt resistor value (Reg 276) must match the actual shunt resistor on Input 5 (Ω).
95 | Holding | Input 6 – Current | UINT16 | RO | - | 0 to 65535 | A | 0.001 | 1 | Measured input current in amperes (A) from Input 6 (scale by 0.001). Valid only when Input Mode 6 (Reg 271) is 1. Shunt resistor value (Reg 277) must match the actual shunt resistor on Input 6 (Ω).
Readable & Writable Registers
128 | Holding | Boot Flag | UINT16 | RW | 1 | 0 to 1 | - | 1 | 1 | This flag is set to 1 when the system starts and may need to be reset to 0 by the user for custom input logic. See Note *2 for a detailed explanation and examples.
129 | Holding | Relay 1 | UINT16 | RW | 0 | 0 to 1 | - | 1 | 1 | Controls Relay 1: 0 for OFF, 1 for ON.
130 | Holding | Relay 2 | UINT16 | RW | 0 | 0 to 1 | - | 1 | 1 | Controls Relay 2: 0 for OFF, 1 for ON.
131 | Holding | Relay 3 | UINT16 | RW | 0 | 0 to 1 | - | 1 | 1 | Controls Relay 3: 0 for OFF, 1 for ON.
132 | Holding | Relay 4 | UINT16 | RW | 0 | 0 to 1 | - | 1 | 1 | Controls Relay 4: 0 for OFF, 1 for ON.
135 | Holding | Relay Timer Register 1 | UINT16 | RW | 0 | 1 to 65536 | Seconds | 1 | 1 | Controls Relay 1 by time: - Turns the relay ON for a specified period. - Example: Writing 300 turns the relay on for 300 seconds.
136 | Holding | Relay Timer Register 2 | UINT16 | RW | 0 | 1 to 65536 | Seconds | 1 | 1 | Controls Relay 2 by time: - Turns the relay ON for a specified period. - Example: Writing 300 turns the relay on for 300 seconds.
137 | Holding | Relay Timer Register 3 | UINT16 | RW | 0 | 1 to 65536 | Seconds | 1 | 1 | Controls Relay 3 by time: - Turns the relay ON for a specified period. - Example: Writing 300 turns the relay on for 300 seconds.
138 | Holding | Relay Timer Register 4 | UINT16 | RW | 0 | 1 to 65536 | Seconds | 1 | 1 | Controls Relay 4 by time: - Turns the relay ON for a specified period. - Example: Writing 300 turns the relay on for 300 seconds.
141 | Holding | 0-10V Channel Output 1 | UINT16 | RW | 0 | 0 to 10000 | Volts | 0.001/0.01 | 1 | Controls voltage output 1 (0–10 V or 1–10 V, per Reg 290). Unit and scaling depend on mode: - V mode: write mV × 1, range 0…10000, multiplier 0.001 (e.g., 5000 → 5.000 V). - % mode: write % × 100, range 0…10000, multiplier 0.01 (e.g., 5000 → 50.00%).
142 | Holding | 0-10V Channel Output 2 | UINT16 | RW | 0 | 0 to 10000 | Volts | 0.001/0.01 | 1 | Controls voltage output 2 (0–10 V or 1–10 V, per Reg 291). Unit and scaling depend on mode: - V mode: write mV × 1, range 0…10000, multiplier 0.001 (e.g., 5000 → 5.000 V). - % mode: write % × 100, range 0…10000, multiplier 0.01 (e.g., 5000 → 50.00%).
143 | Holding | 4-20mA Channel Output 1 | UINT16 | RW | 0 | 0 to 20000 | Milliamps (mA) | 0.001/0.01 | 1 | Controls current output 1 (0–20 mA or 4–20 mA, per Reg 292). Unit and scaling depend on mode: - mA mode: write mA × 1000, range 0…20000, multiplier 0.001 (e.g., 20000 → 20.000 mA). - % mode: write % × 100, range 0…10000, multiplier 0.01 (e.g., 5000 → 50.00%).
144 | Holding | 4-20mA Channel Output 2 | UINT16 | RW | 0 | 0 to 20000 | Milliamps (mA) | 0.001/0.01 | 1 | Controls current output 2 (0–20 mA or 4–20 mA, per Reg 293). Unit and scaling depend on mode: - mA mode: write mA × 1000, range 0…20000, multiplier 0.001 (e.g., 20000 → 20.000 mA). - % mode: write % × 100, range 0…10000, multiplier 0.01 (e.g., 5000 → 50.00%).
191 | Holding | Reboot | UINT16 | RW | 0 | 0 to 65536 |  | 1 | 1 | Reboot the controller Writing any non-zero value triggers an immediate reboot.
192 | Holding | Rule0_RW0 |  | RW |  |  |  | 1 | 1 | Runtime register 0 for Rule 0 See 'Rule Definitions' sheet for details.
193 | Holding | Rule0_RW1 |  | RW |  |  |  | 1 | 1 | Runtime register 1 for Rule 0 See 'Rule Definitions' sheet for details.
194 | Holding | Rule0_RW2 |  | RW |  |  |  | 1 | 1 | Runtime register 2 for Rule 0 See 'Rule Definitions' sheet for details.
195 | Holding | Rule0_RW3 |  | RW |  |  |  | 1 | 1 | Runtime register 3 for Rule 0 See 'Rule Definitions' sheet for details.
|  | RuleX_RWn | [7 empty] | Remaining rules' runtime registers follow the same 4 register layout. Address = 192 + (X × 4 + n) where X = rule number (0–15), n = register index (0-3). A total of 16 rules are supported. See 'Rule Definitions' sheet for details.
Configuration Registers
256 | Holding | Modbus Address | UINT16 | RW | 1 | 1 to 247 | - | 1 | 1 | Sets the Modbus network address of the controller.
257 | Holding | Baud Rate | UINT16 | RW | 6 | 1 to 10 | - | 1 | 1 | Sets the communication baud rate. Options: 1 - (300 bps) 2 - (600 bps) 3 - (1200 bps) 4 - (2400 bps) 5 - (4800 bps) 6 - (9600 bps) 7 - (19200 bps) 8 - (38400 bps) 9 - (57600 bps) 10 - (115200 bps)
258 | Holding | Character Framing | UINT16 | RW | 1 | 1 to 4 | - | 1 | 1 | Configures Modbus character framing: 1 - (8E1): 8 bits, Even parity, 1 stop bit. 2 - (8N2): 8 bits, No parity, 2 stop bits. 3 - (8N1): 8 bits, No parity, 1 stop bit. 4 - (8O1): 8 bits, Odd parity, 1 stop bit.
264 | Holding | Relay Coil Voltage Reduction | UINT16 | RW | 1 | 0 to 1 | - | 1 | 1 | Configures the operational mode of Relay Coil Voltage Reduction: 0 - Coil reduction OFF (Relay coil operates at full voltage) 1 - Coil reduction ON (Reduces relay coil voltage after activation to save power)
265 | Holding | Buttons Mode | UINT16 | RW | 1 | 0 to 3 | - | 1 | 1 | Configures the operational mode of interface buttons: 0 - Disabled 1 - Enabled (each button toggles its corresponding relay) 2 - Offline Mode (each button toggles its corresponding relay if no Master query for 60s) 3 - Relay Disable Mode - When activated via button, the corresponding relay turns off, and its LED starts flashing. - The relay cannot be operated via Modbus while in this state. - Pressing the button again restores the relay to the state defined in the relay register. - Note: After a controller reboot, any active relay disablements will be cleared.
266 | Holding | Input 1 Mode | UINT16 | RW | 1 | 0, 1, 10, 11 | - | 1 | 1 | Sets the operational mode for Input 1: 0 - Switchable pull-up activated for reliable digital dry contact detection. 1 - Switchable pull-up deactivated, suitable for external analog signal measurements, like 0-10V or 4-20mA signals. 10 - NTC 10K, β=3435. 11 - NTC 10K, β=3977 (NTC modes automatically manage the pull-up circuit for accurate measurement).
267 | Holding | Input 2 Mode | UINT16 | RW | 1 | 0, 1, 10, 11 | - | 1 | 1 | Sets the operational mode for Input 2: 0 - Switchable pull-up activated for reliable digital dry contact detection. 1 - Switchable pull-up deactivated, suitable for external analog signal measurements, like 0-10V or 4-20mA signals. 10 - NTC 10K, β=3435. 11 - NTC 10K, β=3977 (NTC modes automatically manage the pull-up circuit for accurate measurement).
268 | Holding | Input 3 Mode | UINT16 | RW | 1 | 0, 1, 10, 11 | - | 1 | 1 | Sets the operational mode for Input 3: 0 - Switchable pull-up activated for reliable digital dry contact detection. 1 - Switchable pull-up deactivated, suitable for external analog signal measurements, like 0-10V or 4-20mA signals. 10 - NTC 10K, β=3435. 11 - NTC 10K, β=3977 (NTC modes automatically manage the pull-up circuit for accurate measurement).
269 | Holding | Input 4 Mode | UINT16 | RW | 1 | 0, 1, 10, 11 | - | 1 | 1 | Sets the operational mode for Input 4: 0 - Switchable pull-up activated for reliable digital dry contact detection. 1 - Switchable pull-up deactivated, suitable for external analog signal measurements, like 0-10V or 4-20mA signals. 10 - NTC 10K, β=3435. 11 - NTC 10K, β=3977 (NTC modes automatically manage the pull-up circuit for accurate measurement).
270 | Holding | Input 5 Mode | UINT16 | RW | 1 | 0, 1, 10, 11 | - | 1 | 1 | Sets the operational mode for Input 5: 0 - Switchable pull-up activated for reliable digital dry contact detection. 1 - Switchable pull-up deactivated, suitable for external analog signal measurements, like 0-10V or 4-20mA signals. 10 - NTC 10K, β=3435. 11 - NTC 10K, β=3977 (NTC modes automatically manage the pull-up circuit for accurate measurement).
271 | Holding | Input 6 Mode | UINT16 | RW | 1 | 0, 1, 10, 11 | - | 1 | 1 | Sets the operational mode for Input 6: 0 - Switchable pull-up activated for reliable digital dry contact detection. 1 - Switchable pull-up deactivated, suitable for external analog signal measurements, like 0-10V or 4-20mA signals. 10 - NTC 10K, β=3435. 11 - NTC 10K, β=3977 (NTC modes automatically manage the pull-up circuit for accurate measurement).
272 | Holding | Input 1 Shunt Resistor | UINT16 | RW | 250 | 1 to 1000 | - | 1 | 1 | Sets the shunt resistor value in ohms for Input 1. Used for current measurement when Input 1 Mode (Reg 266) = 1 (analog). Enter the actual resistor installed.
273 | Holding | Input 2 Shunt Resistor | UINT16 | RW | 250 | 1 to 1000 | - | 1 | 1 | Sets the shunt resistor value in ohms for Input 2. Used for current measurement when Input 2 Mode (Reg 267) = 1 (analog). Enter the actual resistor installed.
274 | Holding | Input 3 Shunt Resistor | UINT16 | RW | 250 | 1 to 1000 | - | 1 | 1 | Sets the shunt resistor value in ohms for Input 3. Used for current measurement when Input 3 Mode (Reg 268) = 1 (analog). Enter the actual resistor installed.
275 | Holding | Input 4 Shunt Resistor | UINT16 | RW | 250 | 1 to 1000 | - | 1 | 1 | Sets the shunt resistor value in ohms for Input 4. Used for current measurement when Input 4 Mode (Reg 269) = 1 (analog). Enter the actual resistor installed.
276 | Holding | Input 5 Shunt Resistor | UINT16 | RW | 250 | 1 to 1000 | - | 1 | 1 | Sets the shunt resistor value in ohms for Input 5. Used for current measurement when Input 5 Mode (Reg 270) = 1 (analog). Enter the actual resistor installed.
277 | Holding | Input 6 Shunt Resistor | UINT16 | RW | 250 | 1 to 1000 | - | 1 | 1 | Sets the shunt resistor value in ohms for Input 6. Used for current measurement when Input 6 Mode (Reg 271) = 1 (analog). Enter the actual resistor installed.
290 | Holding | 0–10 V Output 1 Mode | UINT16 | RW | 0 | 0,1,2,3 | - | 1 | 1 | Sets the operational mode for 0–10 V Output 1: 0 – 0–10 V range 1 – 1–10 V range 2 – 0–10 V range, % scaling 3 – 1–10 V range, % scaling
291 | Holding | 0–10 V Output 2 Mode | UINT16 | RW | 0 | 0,1,2,3 | - | 1 | 1 | Sets the operational mode for 0–10 V Output 2: 0 – 0–10 V range 1 – 1–10 V range 2 – 0–10 V range, % scaling 3 – 1–10 V range, % scaling
292 | Holding | 4–20 mA Output 1 Mode | UINT16 | RW | 1 | 0,1,2,3 | - | 1 | 1 | Sets the operational mode for 4–20 mA Output 1: 0 – 0–20 mA range 1 – 4–20 mA range 2 – 0–20 mA range, % scaling 3 – 4–20 mA range, % scaling
293 | Holding | 4–20 mA Output 2 Mode | UINT16 | RW | 1 | 0,1,2,3 | - | 1 | 1 | Sets the operational mode for 4–20 mA Output 2: 0 – 0–20 mA range 1 – 4–20 mA range 2 – 0–20 mA range, % scaling 3 – 4–20 mA range, % scaling
Rule Configuration Registers
1000 | Holding | Rule0_Type | UINT16 | RW | 0 | 0 to 65536 | - | 1 | 1 | See 'Rule Definitions' sheet
1001 | Holding | Rule0_Param0 | UINT16 | RW | 0 | 0 to 65536 | - | 1 | 1 | See 'Rule Definitions' sheet
1002 | Holding | Rule0_Param1 | UINT16 | RW | 0 | 0 to 65536 | - | 1 | 1 | See 'Rule Definitions' sheet
1003 | Holding | Rule0_Param2 | UINT16 | RW | 0 | 0 to 65536 | - | 1 | 1 | See 'Rule Definitions' sheet
1004 | Holding | Rule0_Param3 | UINT16 | RW | 0 | 0 to 65536 | - | 1 | 1 | See 'Rule Definitions' sheet
1005 | Holding | Rule0_Param4 | UINT16 | RW | 0 | 0 to 65536 | - | 1 | 1 | See 'Rule Definitions' sheet
1006 | Holding | Rule0_Param5 | UINT16 | RW | 0 | 0 to 65536 | - | 1 | 1 | See 'Rule Definitions' sheet
1007 | Holding | Rule0_Param6 | UINT16 | RW | 0 | 0 to 65536 | - | 1 | 1 | See 'Rule Definitions' sheet
1008 | Holding | Rule0_Param7 | UINT16 | RW | 0 | 0 to 65536 | - | 1 | 1 | See 'Rule Definitions' sheet
1009 | Holding | Rule0_Param8 | UINT16 | RW | 0 | 0 to 65536 | - | 1 | 1 | See 'Rule Definitions' sheet
|  | RuleX_Type / RuleX_ParamN | UINT16 | RW | 0 | 0 to 65536 | - | 1 | 1 | Remaining rules follow same structure every 10 registers. Address = 1000 + (X × 10) where X = rule number (0–15). A total of 16 rules are supported.
Rule Configuration Registers
9000 | Holding | FW_Block_Write | BYTE[130] | W |  |  | - | 1 | 65 | See 'Firmware Update' sheet
Note *1: Active/Inactive State Description for Digital Inputs - Active State: Defined by a voltage level in the range of 0 to 0.8V - Inactive State: Defined by a voltage level in the range of 1.8V to 30V
Note *2: Custom Input Logic: Bit 0: Input State - Represents the current real-time physical state of the input (0 = inactive, 1 = active). Bits 1-4: Activation Counter - Increments each time the input transitions to the active state. Bit 5: Input Change Flag - Set to 1 for 30 seconds following any change in input state, indicating recent activity. Bit 6: Boot State Indicator - Reflects the boot register (reg 128) state (1 = device has rebooted). Bits 7-9: Single Click Counter - Increments each time a single click is identified. The system evaluates the input after a 350ms window to determine if a single click occurred within this period. Bits 10-12: Double Click Counter - Increases for two quick presses: the first within 350ms, followed by a second in another 350ms window. Double-click registered if both fit this timing Bits 13-15: Long Push Counter - Increments when the input is held in the active state for longer than 2 seconds, indicating a long press.

## Rule Definitions
Internal Rule Engine Configuration
Rule Type Summary
Rule Type | Name | Description
0 | Disabled | Rule is not active
1 | Toggle Relay Rule | Toggles relay via corresponding input
2 | Flexible Switch Control Rule | Bitmask-based input/relay control
10 | Thermostat Control | Relay control based on temperature
11 | Analog Threshold Control | Relay control based on analog voltage
100 | Voltage Failover Rule | Analog output follows input unless overridden via external control
⚠️ Configuration Note (Important)
When configuring or modifying a rule, always write to the RuleX_Type register last. - Writing a non-zero value to RuleX_Type activates the rule - Writing 0 disables the rule - Parameter changes are only applied if the rule is disabled before modification and re-enabled afterward
Rule Type 1 - Toggle Relay Rule
This rule links selected input channels to their corresponding relays (e.g., input 1 toggles relay 1), with control logic defined by switch type.
Configuration Parameters
Parameter Index | Name | Description
Type |  | Must be set to 1
Param0 | Input Enable Bitmask | Each bit enables an input (bit 0 = input 1, bit 1 = input 2, etc.)
Param1 | Switch Type | 0 = Toggle switch, 1 = Push button
Example: Toggle Relay Rule (Rule Slot 0)
Use case: Toggling a wall switch connected to Input 1 changes the state of Relay 1 (like a standard light switch).
Register | Name | Value | Description
1000 | Rule0_Type | 1 | Toggle Relay Rule
1001 | Rule0_Param0 | 1 | Enable Input 1 (bit 0)
1002 | Rule0_Param1 | 0 | Toggle switch mode
Behavior:
Relay 1 switches ON or OFF each time the wall switch is toggled.
Rule Type 2 – Flexible Switch Control Rule
This rule enables multiple inputs to control one or more relays, with independent configuration for switch type and optional timer-based reset.
Configuration Parameters
Parameter Index | Name | Description
Type |  | Must be set to 2
Param0 | Toggle Input Bitmask | Each bit enables a toggle input (bit 0 = input 1, bit 1 = input 2, etc.)
Param1 | Push Button Input Bitmask | Each bit enables a push-button input (bit 0 = input 1, bit 1 = input 2, etc.)
Param2 | Relay Output Bitmask | Each bit defines a controlled relay (bit 0 = relay 1, bit 1 = relay 2, etc.)
Param3 | Countdown Time | In seconds. If zero, relays toggle OFF on second press. If non-zero, relays turn OFF automatically after time elapses. If a new input activation occurs while the countdown is active, the timer restarts from the original value.
Example: Flexible Switch Control (Rule Slot 1)
Use case: Two wall switches (connected to Input 2 and Input 3) control Relay 2.
Each switch acts as a toggle. When the relay turns ON, it automatically turns OFF after 60 seconds.
Register | Name | Value | Description
1010 | Rule1_Type | 2 | Toggle Relay Rule
1011 | Rule1_Param0 | 6 | Inputs 2 & 3 as toggles (bitmask: bits 1 and 2)
1012 | Rule1_Param1 | 0 | No push buttons
1013 | Rule1_Param2 | 2 | Relay 2 (bit 1)
1014 | Rule1_Param3 | 60 | Countdown 60s
Behavior:
Toggling either wall switch changes the state of Relay 2. If the relay is turned ON, a 60-second countdown starts. If a new switch activation occurs during the countdown, the timer restarts from 60 seconds. Once the countdown ends, Relay 2 turns OFF automatically.
Rule Type 10 – Thermostat Control
This rule activates or deactivates selected relays based on the temperature value from the corresponding temperature input. The rule uses a configured setpoint and hysteresis band to determine when outputs should switch ON or OFF. The input must be configured in NTC mode (type 10 or 11) to provide a valid measurement.
Configuration Parameters
Parameter Index | Name | Description
Type |  | Must be set to 10
Param0 | Temperature Input Channel | Selects which input channel to use (e.g., 2 = Input 2) The selected input must be configured in NTC mode (10 or 11).
Param1 | Relay Output Bitmask | Each bit enables an output relay (bit 0 = relay 1, bit 1 = relay 2, etc.)
Param2 | Setpoint Temperature | Setpoint temperature (°C), value is multiplied by 0.01 (e.g., 2250 = 22.50 °C)
Param3 | Hysteresis | Hysteresis (°C), value is multiplied by 0.01 (e.g., 50 = 0.50 °C)
Param4 | Mode | 0 = Heating (Activate Below) – relay turns ON when value is below (setpoint − hysteresis), and OFF when it reaches the setpoint. 1 = Cooling (Activate Above) – relay turns ON when value is above (setpoint + hysteresis), and OFF when it drops to the setpoint.
Example: Thermostat Control (Rule Slot 2)
Use case: NTC on Input 4 controls Relay 3 for heating.
Register | Name | Value | Description
1020 | Rule2_Type | 10 | Thermostat Rule
1021 | Rule2_Param0 | 4 | Use Temperature channel 4
1022 | Rule2_Param1 | 4 | Relay 3 (bit 2)
1023 | Rule2_Param2 | 2250 | Setpoint = 22.50 °C
1024 | Rule2_Param3 | 50 | Hysteresis = 0.50 °C
1025 | Rule2_Param4 | 0 | Heating mode
Behavior:
Relay 3 turns ON when the temperature from Input 4 drops below the setpoint minus hysteresis. It turns OFF once the temperature rises to or above the setpoint. For example, with a setpoint of 22.50 °C and hysteresis of 0.50 °C: Relay turns ON below 22.00 °C Relay turns OFF at or above 22.50 °C
Rule Type 11 – Analog Threshold Control
This rule monitors an analog input voltage and switches relays based on threshold logic with hysteresis.
Configuration Parameters
Parameter Index | Name | Description
Type |  | Must be set 11
Param0 | Analog Input Channel | Selects which analog input to use (1–6)
Param1 | Relay Output Bitmask | Each bit enables an output relay (bit 0 = relay 1, bit 1 = relay 2, etc.)
Param2 | Setpoint Value | Voltage threshold, value is multiplied by 0.01 (e.g., 250 = 2.50 V)
Param3 | Hysteresis | Hysteresis (V), value is multiplied by 0.01 (e.g., 50 = 0.50 V)
Param4 | Mode | 0 = Activate Below – relay turns ON when value is below (setpoint − hysteresis), and OFF when it reaches the setpoint. 1 = Activate Above – relay turns ON when value is above (setpoint + hysteresis), and OFF when it drops to the setpoint.
Example: Thermostat Control (Rule Slot 3)
Use case: Input 5 (0–10 V) controls Relay 4 above 6.5 V.
Register | Name | Value | Description
1030 | Rule3_Type | 11 | Analog Threshold Rule
1031 | Rule3_Param0 | 5 | Use Analog Input 5
1032 | Rule3_Param1 | 8 | Relay 4 (bit 3)
1033 | Rule3_Param2 | 650 | Setpoint = 6.50V
1034 | Rule3_Param3 | 50 | Hysteresis = 0.50V
1035 | Rule3_Param4 | 1 | Active Above
Behavior:
Relay 4 turns ON when the voltage from Input 5 rises above the setpoint plus hysteresis. It turns OFF once the voltage drops to or below the setpoint. For example, with a setpoint of 6.50 V and hysteresis of 0.50 V: Relay turns ON above 7.00 V Relay turns OFF at or below 6.50 V
Rule Type 100 – Communication-Driven Voltage Failover Control
This rule allows an analog voltage output to mirror an input voltage unless overridden by a remote command. It is typically used in Virtual Power Plant (VPP) applications to override local control when external control is needed. Each channel has a timeout: if the external override is not refreshed in time, the output returns to following the input voltage.
Configuration Parameters
Parameter Index | Name | Description
Type |  | Must be set 100
Param0 | Channel Enable Bitmask | Bit 0 = Channel 1 voltage output (0–10V), Bit 1 = Channel 2 voltage output (0–10V)
Param1 | CH1 Timeout | Time in seconds that external control (setpoint write) is valid. Must be ≥ 1. If the runtime value is not updated within this period, the output reverts to following the analog input.
Param2 | CH2 Timeout | Time in seconds that external control (setpoint write) is valid. Must be ≥ 1. If the runtime value is not updated within this period, the output reverts to following the analog input.
Runtime Data
Register Offset | Name | Description
RuleX_RW0 | CH1 Setpoint | Analog voltage output setpoint for Channel 1 (0-10 V). Written as a UINT16 where 10000 = 10.000 V. Must be updated regularly to maintain override.
RuleX_RW1 | CH2 Setpoint | Analog voltage output setpoint for Channel 2 (0-10 V). Written as a UINT16 where 10000 = 10.000 V. Must be updated regularly to maintain override.
Notes: - If a value is written to RuleX_RW0 or RuleX_RW1, the corresponding output is immediately set to that voltage. - The controller tracks how long it has been since the last update.If the configured timeout expires, the channel output will revert to mirroring the analog input. - For continuous remote control, the runtime register must be updated periodically within the timeout window.
Example: Voltage Failover Control (Rule Slot 4)
Use case: Controller mirrors analog input to analog output by default. When a remote system writes a new voltage setpoint to the runtime register, the controller overrides the output for a defined period. After the timeout expires without refresh, the output returns to input tracking.
Register | Name | Value | Description
1040 | Rule4_Type | 100 | Voltage Failover Rule
1041 | Rule4_Param0 | 3 | Enable CH1 and CH2 (bit 0 = CH1, bit 1 = CH2)
1042 | Rule4_Param1 | 5 | CH1 timeout = 5 seconds
1043 | Rule4_Param2 | 10 | CH2 timeout = 10 seconds
Behavior:
Default behavior: CH1 and CH2 outputs follow their respective analog input voltages.
Remote override: Writing a value (e.g., 6000 = 6.000 V) to Rule4_RW0 (register 208) or Rule4_RW1 (register 209) overrides the output voltage.
The override remains valid for the configured timeout duration.
If no new value is written before timeout, the controller reverts output back to tracking the input.
Example:
- Remote system writes 5000 to Rule4_RW0 (register 208) → CH1 output is set to 5.000 V.
- If not refreshed within 5 seconds, CH1 returns to mirroring the analog input.

## Firmware Update
Firmware Update via Modbus RTU
Firmware updates are performed by sending 128-byte blocks to a dedicated Modbus register. Each block must be exactly 130 bytes: - 2 bytes for the block offset (high byte + low byte) - 128 bytes of firmware data
The block offset defines the write position of the firmware data in flash memory. Offset 0 means the first 128 bytes of the firmware file, offset 1 means the second 128 bytes, and so on.
The controller writes each block to flash as it is received. Once the final block is received, the controller will reboot automatically after a 5-second delay.
Address | Name | Description | Data Type | Access
9000 | FW_Block_Write | Firmware update block write interface | BYTE[130] | Write-only
Block Format
Byte Index | Purpose
0 | Offset High Byte (block offset >> 8)
1 | Offset Low Byte (block offset & 0xFF)
2-129 | 128 bytes of firmware data
⚠️ Important Notes
- Each firmware block must be exactly 130 bytes in total. - If the final firmware block is smaller than 128 bytes, it must be padded with 0x00 or any other value. - CRC validation is handled by the Modbus protocol itself; no additional checksum is needed. - The controller will automatically reboot 5 seconds after receiving the final block.
This process ensures a reliable and compact mechanism to perform firmware upgrades in the field using the standard Modbus RTU protocol.

## Communications Examples
Practical Examples of Modbus RTU Communications
Here are some practical examples of Modbus RTU communications, detailing the packet structure necessary for reading from and writing to the FoxIoT controller's registers. These illustrate how to construct the packets for: - Reading an analog value from Input 1 (UINT16). - Reading the state of a digital input from Input 2 (UINT16). - Setting the state of Relay 1 and Relay 2. - Setting the Modbus address of the controller. Each Modbus RTU packet includes a device address, function code, data payload (which encompasses register addresses and values), and a Cyclic Redundancy Check (CRC) for error checking.
Example 1: Read Analog Input from Input 1
To retrieve the analog value of input 1, we use the following Modbus RTU packet: Request: This request packet in bytes is: 01 03 00 2A 00 01 A5 C2 - Device Address: 01 (The Modbus device address) - Function Code: 03 (Function code for reading holding registers) - Register Address: 002A (The address of the analog input 1 register, 42 in decimal)) - Quantity of Registers: 0001 (Number of registers to read) - CRC: A5C2 (The error-checking CRC value) Response: This response packet in bytes is: 01 03 02 13 88 B5 12 - Device Address: 01 (The Modbus device address) - Function Code: 03 (Function code for reading holding registers) - Byte Count: 02 (Number of data bytes to follow) - Data: 1388 (The data retrieved from the input register) - CRC: B512 (The error-checking CRC value) The response indicates that the value retrieved from register 42 is 0x1388. To convert this value to the actual voltage, multiply it by the scaling factor of 0.001 (as per the register description). This means the voltage reading from Input 1 - Analog is 5.000 volts (if we interpret 0x1388 as 5000 in decimal).
Example 2: Reading Digital Input from Input 2
To retrieve the digital state of input 2, we use the following Modbus RTU packet: Request: This request packet in bytes is: 01 03 00 31 00 01 D5 C5 - Device Address: 01 (The Modbus device address) - Function Code: 03 (Function code for reading holding registers) - Register Address: 0031 (The address of the digital input register, 49 in decimal) - Quantity of Registers: 0001 (Number of registers to read) - CRC: D5C5 (The error-checking CRC value) Response: This response packet in bytes is: 01 03 02 00 01 79 84 - Device Address: 01 (The Modbus device address) - Function Code: 03 (Function code for reading holding registers) - Byte Count: 02 (Number of data bytes to follow) - Data: 0001 (The data retrieved from the input register) - CRC: 7984 (The error-checking CRC value) The response data 0x0001 from Register 49 (0x31) indicates that input 2 is in an active state.
Example 3: Controlling Relay 1 and Relay 2 States
To simultaneously control the state of Relay 1 and Relay 2, we use the following Modbus RTU packet: Request: This request packet in bytes is: 01 10 00 81 00 02 04 00 01 00 00 6B C3 - Device Address: 01 (The Modbus device address) - Function Code: 10 (Function code for writing multiple holding registers) - Register Address: 0081 (The starting address for the operation, corresponding to Relay 1's register, which is 129 in decimal) - Quantity of Registers: 0002 (Indicates that two registers will be written to, covering Relay 1 and Relay 2) - Byte Count: 04 (Indicates 4 bytes of data for 2 registers (2 bytes per register)) - Data for Relay 1: 0001 (Data to set the state of Relay 1. In this example, 01 sets Relay 1 to the ON state) - Data for Relay 2: 0000 - (Data to set the state of Relay 2. In this example, 00 sets Relay 2 to the OFF state) - CRC: 6BC3 (The error-checking CRC value) Response: This response packet in bytes is: 01 10 00 81 00 02 11 E0 - Device Address: 01 (Identifies the Modbus device address) - Function Code: 10 (Confirms the operation was to write to multiple holding registers) - Register Address: 0081 (Echoes the starting address from the request, corresponding to Relay 1's register) - Quantity of registers: 0002 (Confirms that two registers were targeted, as per the request, affecting Relay 1 and Relay 2) - CRC: 11E0 (The error-checking CRC value) The response packet confirms the successful execution of the command to write to multiple holding registers, ensuring that Relay 1 and Relay 2 are set as requested.